Specification for

PV & Storage Inverter Interactions using IEC 61850 Object Models and Capabilities

(Draft v12f)

Table of Contents

1.	Overview	1

1.1	Background of EPRI's Photovoltaic & Storage Integration Program	1

1.2	Introduction to the Specification	1

1.3	Different PV/Storage Inverter Management Methods	2

1.3.1	Directly Managed PV Systems	2

1.3.2	Interactive Control of Autonomous PV Inverters	3

1.3.3	Broadcast or Multicast Requests to Groups of PV Inverters	4

1.4	Differing DER Architectures	4

1.4.1	Conceptual Architecture: Electrical Coupling Point (ECP)	4

1.4.2	Utility Interactions Indirectly with PV Inverters via a Customer EMS	5

1.4.3	Utility Interactions Directly with PV Inverter Controllers	6

1.5	General Sequence of Interactions	7

1.6	Levels of Compliance with this Specification	9

2.	Control Functions for PV Inverters	10

2.1	Basic Control PV Inverter Functions	10

2.1.1	Function PC1: Connect / Disconnect from Grid	10

2.1.2	Function PC2: Adjust Maximum Generation Level Up/Down	11

2.1.3	Function PC3: Adjust Power Factor	11

2.2	PV/Storage Functions	12

2.2.1	Function PC4a: Request Real Power (Charge or Discharge Storage)	12

2.2.2	Function PC4b: Provide Pricing Signal	13

2.2.3	Function PC4c: Modify PV/Storage Settings	14

2.3	Reporting Functions	14

2.3.1	Function PC5: Event/History Logging	14

2.3.2	Function PC6: Status Reporting	16

2.4	Periodic Commands	17

2.4.1	Function PC7: Time Synchronization	17

2.5	VAR Modes for Decentralized Var Support from PV/Storage Inverters	18

2.5.1	VAR Management Modes and Volt/Var Arrays (SubModes)	18

2.5.2	VAR Mode PV1: Normal Energy Conservation Mode	19

2.5.3	VAR Mode PV2: Maximum Var Support Mode	20

2.5.4	VAR Mode PV3: Static Var Mode	22

2.5.5	VAR Mode PV4: Passive Mode	23

3.	Scheduled Actions	25

3.1	Scheduling Using Time and Temperature for Var Modes	25

3.2	Scheduling for Charging / Discharging in PV/Storage Systems	26

3.3	Scheduling Using Pricing Signals (or Value) of Energy	26

# Overview

## Background of EPRI's Photovoltaic & Storage Integration Program

In 2009, EPRI’s Photovoltaic & Storage Integration Program (P174) began a series of studies related to the high penetration of distributed energy resources (DER). One research area in this program is specifically focused on the communication aspects of DER integration. This research led, in mid 2009, to the launch of a broad industry collaborative to identify a common means by which smart, communicating inverters may be integrated into utility systems.

The Department of Energy, Sandia National Laboratories, and the Solar Electric Power Association have been historically active in this area of study and have joined with EPRI in steering the overall project. At the present (February 2010), the project has engaged 350 individuals representing inverter providers, utilities, and research organizations.

The central goal of the project is to identify a core set of common inverter capabilities that, if made available, may enable higher penetration levels and enhance the value of grid-tied PV and storage devices. By working closely with the community of inverter manufacturers, the project hopes to allow for innovation and evolution of devices, while at the same time making it possible to standardize communication messages for those functions that are common.

The project was formally kicked-off at a workshop held in Albuquerque, NM during the DOE’s SEGIS-ES conference. At that workshop, a large range of use cases that had been previously collected were down-selected into seven functions that were deemed most needed. More detail about the project history is included in a previous update that was published as Report # 1020435 (available at epri.com).

## Introduction to the Specification

These specifications cover interactions between utilities (or their surrogate energy service providers (ESP)) and PV/Storage systems. The PV systems can range from 1) very small grid-connected PV systems at residential customer sites, tied into the grid through net metering to 2) medium PV systems managing campus or community PVs to 3) very large PV plants. These PV systems may or may not include DC-connected energy storage capabilities as integral parts of their management. The focus is on PV inverter management and does not cover any other types of energy management.

These specifications cover a limited set of functions in an attempt to take baby steps before trying to define a larger and/or more complex set of functions. Therefore, in no way do these functions try to limit what can be tried or implemented beyond them – the key idea is that IF the functions covered in this specification are implemented, THEN they will be implemented as specified below.

## Different PV/Storage Inverter Management Methods

There are three methods to manage PV/storage inverters:

- Direct management by a PV controller of a specific PV inverter: tightly coupled commands assuming complete knowledge of the PV inverter status and capabilities

- Interactive management of PV controllers: loosely-coupled requests assuming key knowledge of current PV inverter status, but allowing the autonomous PV controller to accept, not accept, or modify the request based its internal knowledge of the inverter or storage unit capabilities. The PV controller provides feedback to the requester.

- Broadcasting or multicasting to specific types/sizes/regions of PV inverters: open requests without the expectation of any directly communicated responses. Only changes in the power system (voltage, vars, load level, etc.) and the eventual metering of the PV inverter provide feedback.

The latter two methods could issue single control requests or could provide a schedule of control requests based on time, temperature, pricing signal, or other parameters.

These different PV management interactions are shown in the general DER system illustrated below.

### Directly Managed PV Systems

Directly managed PV systems have their components (inverters, PV panels, storage, etc.) directly monitored and controlled by a separate controller. With managed PV systems, the intelligence that makes the PV settings and the storage charge/discharge decisions is in the separate controller. This separate controller can issue settings, get status information, monitor measured values, and command control actions of specific PV inverters with the expectation of communicated replies acknowledging the commands and providing the status and/or response information. This method provides tightly-coupled control, and requires active and rapid interactions between the controller and the PV inverter.

This separate controller may receive requests and other information from external systems (such as  a customer EMS, a utility, or an energy service provider). The controller may also, depending upon its capabilities, utilize schedules of energy prices, weather forecasts, expected customer requirements for stored energy at different times, etc. to determine what direct control commands it will issue to the PV inverter or other component.

Examples of direct commands include:

Connect/disconnect from grid (see PC1)

Charge to % of capacity at specified ramp rate or for specified length of time (see PC4a)

Discharge to % of capacity at specified ramp rate or for specified length of time (see PC4a)

Pricing signal to provide information for autonomous PV/Storage system on which to make charging/discharging decisions.

The communications between such a separate controller and the components it is controlling may be proprietary if it is provided as a turn-key integrated “autonomous” system. If, however, the controller and the PV inverter are provided separately, then communication standards should be used.

### Interactive Control of Autonomous PV Inverters

Autonomous PV systems locally manage their own settings, including charging and discharging of any energy storage units. They use both local data and general information that may be provided to the system.  General information might include schedules of energy prices, weather forecasts, expected customer requirements for stored energy at different times, and expected availability of locally produced energy (e.g. PV system).  An example of an autonomous PV system would be a residential customer-owned PV-inverter-and-battery-storage system that is charging and discharging according to preferences set by the customer. Any communications between components of the autonomous system are handled internally. Only communications between the autonomous PV system and external systems would be within the scope of this specification.

An example of a managed PV system would be a utility-owned PV plant (with multiple PV inverters and energy storage units) that is managed via a SCADA system by a centralized control application.

The primary difference between these managed systems and autonomous systems is that the separate controllers would be required to use standards (i.e. IEC 61850) for communicating with the individual components of the PV/storage system, in addition to communications with external systems.

Direct control would typically be utilized for larger PV installations or for utility-owned PV inverters. The utility could send volt/var settings with the request for the PV inverter controller to go to those settings immediately, and the PV inverter would reply directly back to the utility. The utility could periodically update the volt/var settings as needed, such as every few hours.

### Broadcast or Multicast Requests to Groups of PV Inverters

Broadcast or multicast requests would be sent to groups of PV inverters without the expectation of communicated . This broadcast approach would be termed decentralized and “loosely-coupled”.

Broadcasts or multicasts would be used typically for smaller PV inverters. For these smaller PV inverters, the utility would not want to get (or may not be able to get) any explicit response back from the PV inverters on whether or not they responded or by how much. The utility would rely primarily on aggregated response of these PV systems rather than on specific responses by individual PV inverters.

This is an individual design or implementation consideration, based on the need of the utility for precise results. They can see general results as they monitor the power system in real-time, and can assess more specific results much later as they get information from the metering systems.

## Differing DER Architectures

### Conceptual Architecture: Electrical Coupling Point (ECP)

Some PV/Storage  systems may be directly connected to the utility grid, while others may be part of a site microgrid. In either case, the PV/Storage systems will have a point of electrical connection, which is defined as:

“The point of electrical connection between the DER source of energy (generation or storage) and any electric power system (EPS). Each DER (generation or storage) unit has an ECP connecting it to its local power system; groups of DER units have an ECP where they interconnect to the power system at a specific site or plant; a group of DER units plus local loads have an ECP where they are interconnected to the utility power system.

NOTE For those ECPs between a utility EPS and a plant or site EPS, this point is identical to the point of common coupling (PCC) defined in the IEEE 1547 “Standard for Interconnecting Distributed Resources with Electric Power Systems”.

This concept is illustrated in Figure 1.

Figure 1: Electrical Connection Point (ECP)

### Utility Interactions Indirectly with PV Inverters via a Customer EMS

Utilities can interact with PV/Storage systems using different architectures. The following diagram illustrates the use of a Customer EMS to help manage PV inverter responses to the broadcast utility request, with the idea that this Customer EMS will possibly be managing multiple PV inverters, customer appliances, other types of distributed generators and storage devices, and plug-in electric vehicles. For instance, if the utility broadcasts a specific request for PV inverter actions, then these can be passed directly or indirectly (through explicit commands) to the PV inverters. If the utility broadcasts Demand Response signals or more generic volt/var requests, then the Customer EMS could use other devices in addition to PV inverters to meet these requests. With this approach, the Customer EMS could manage responses locally to meet the requests with the most effective mix of devices.

From a communications perspective, the utility broadcast to the customer site, between the utility and the “Customer EMS”, could use different technologies at different layers, for example:

Transport layers: Internet, GPRS, AMI network, private network

Application protocols: Web services, XML-based, ANSI C12.22, DNP3, MMS

Object models: IEC 61850

For the communications within the customer site between the “Customer EMS” and the PV inverter, the following communications technologies could be used at different layers, for example:

Transport layers: ZigBee, HomePlug, Intranet

Application protocols: Web services, XML-based, SEP, MMS

Object models: IEC 61850

Figure 2: Utility interactions with PV inverters via a Customer EMS

### Utility Interactions Directly with PV Inverter Controllers

Alternatively, utilities can communicate requests directly with PV inverter controllers. These requests are then interpreted by the PV inverter controllers.

From a communications perspective, the utility broadcast to the customer site, between the utility and the PV inverter, could use different technologies at different layers, for example:

Transport layers: Internet, GPRS, AMI network, private network

Application protocols: Web services, XML-based, ANSI C12.22, DNP3, MMS

Object models: IEC 61850

Figure 3: Utility interactions directly with PV inverters

## General Sequence of Interactions

The (generic) sequence for interactions between a utility and PV inverters is (see Figure 2 and Figure 3):

- The utility determines what types of services are desired from PV inverters within a region, on a feeder, or in some other area. This determination will be based on assessments of the power system status, abilities of other equipment to perform the required actions (e.g. capacitor banks for var control), market considerations, etc.

- The utility broadcasts a general request that PV inverters (within a region or feeder or other area) go into a specific mode or that certain parameters are set. This request may be sent either to individual PV inverter controllers, or to more general “Customer EMSs” that know how to interpret such requests for the PV inverter controllers that they are managing. In either case, the utility does not necessarily need to know anything about the PV inverter capabilities, current PV status, market or tariff agreements on using the PV system, or desires of the PV owner.

- At each customer site or other facility, the PV inverter controller OR a Customer “energy management system” (EMS) receives and interprets this broadcast utility request.

- If a Customer EMS is used:

  - The Customer EMS interprets the utility request. It determines whether it will take any action, and what the command(s) will be to the PV inverter controller(s) under its control, including responding to any customer overrides or changes. These actions could be explicit commands to each PV inverter it is managing, or could be a schedule of commands if the PV inverter has the ability to handle schedules.

  - The Customer EMS then issues specific commands to the PV inverter(s): First it requests (or already has) the current status of the PV inverter(s), modifies the command if necessary to reflect the status, and then issues the appropriate command.

  - The PV inverter(s) respond to the Customer EMS command, indicating success or rejection, as well as any error codes. In addition, the current status of the PV inverter could be sent if either explicitly requested by the Customer EMS or if it is “automatically” sent as part of the sequence.

  - The Customer EMS may or may not be required to respond to the utility request.

    - If the utility does not expect a direct response, it may both monitor conditions to determine if enough power system changes have occurred and/or read the meter (or meter event log) to determine if the PV inverter responded appropriately.

    - If it does respond, it will acknowledge receipt of the command and returning the appropriate information.

- If a PV inverter controller directly receives the broadcast request from the utility:

  - The PV inverter controller determines internally how best to respond, and performs those actions.

  - The PV inverter controller may or may not respond to the command from the utility with an acknowledge and any appropriate information.

    - If the utility does not expect a direct response, it may both monitor conditions to determine if enough power system changes have occurred and/or read the meter (or meter event log) to determine if the PV inverter responded appropriately.

    - If it does respond, it will acknowledge receipt of the command and returning the appropriate information.

- The PV inverter(s) are metered either individually or via net metering, with their output (in response to the command) captured as part of the metering data. If electric storage is part of the PV system, then it could be metered separately or the PV system as a whole could just be metered. (Metering is out of scope for this document).

- If communications are lost, the PV inverter goes to a default mode, possibly after a timeout period. The default mode, the timeout period, and other parameters for this situation would be established ahead of time.

- Customers can override or modify commands, at any time if they desire.

## Levels of Compliance with this Specification

There will be different levels of compliance with this specification:

Level 1 will include all PV Modes and Functions 1, 2, 3, 5, 6, 7

Level 2 will add Schedules and Function 4.

# Control Functions for PV Inverters

## Basic Control PV Inverter Functions

Basic control functions assume a tightly coupled interaction between the PV inverters and a controlling entity (utility, energy service provider, or Customer EMS). This implies that the controlling entity has knowledge about the capabilities of the PV inverters, can request updates on their current status, can expect the PV inverter to follow the command to the best of their capabilities, and will receive a direct response from the PV inverters on the results from following the command.

Basic commands will supersede each other and any PV Mode commands in effect, based on the time they were issued by the controlling entity.

Basic commands also imply communication channels with high availability between the controlling entity and the PV inverters, since the controlling entity must maintain direct knowledge of the PV inverter status and capabilities. Nonetheless, it is expected that PV inverters will revert to “default” states if communications are unavailable for some pre-specified length of time (implementation dependent).

It is expected that, in general, utilities will use direct controls with larger, utility-owned PV inverters, while ESPs could use direct commands with groups of PV inverters, and Customer EMSs could use direct controls with those PV inverters belonging to the customer. However, other interactions are possible, depending upon business decisions and specific implementations.

### Function PC1: Connect / Disconnect from Grid

This function causes the PV inverter to immediately physically connect or disconnect from the grid via a disconnect switch at the PV inverter’s ECP to the grid.

The utility/ESP or the Customer EMS takes the following actions:

- (Optional) Request status of PV inverter: Request a pre-defined set of the status information, including the status values, the quality flag, and the timestamp of the status (see Function PC6 for details of status points).

- Issue Connect/Disconnect Command to PV inverter:

  - Binary command to open or close a switch.

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the PV inverter will revert to its default status, such as closing the switch to reconnect to the grid (optional – if not included, then default timeout period for this function will be used)

- Receive response to the command:

  - Successful (plus resulting switch position)

  - Rejected (plus reason)

### Function PC2: Adjust Maximum Generation Level Up/Down

This function sets the maximum generation level at the electrical coupling point (ECP) as a percentage of nameplate capacity.

In addition, a ramp rate (power versus time) and a delay time before starting will be included so that not all PV inverters change state abruptly at the same time.

A timeout period is included for reverting to the default state of the PV inverter, to ensure that a missed or lost command does not impact normal operations beyond that timeout period.

The utility/ESP or the Customer EMS takes the following actions:

- (Optional) Request status of PV inverter: Request a pre-defined set of the status information, including the status values, the quality flag, and the timestamp of the status (see Function PC6 for details of status points).

- Issue command to adjust power setpoint:

  - Command to adjust the power setpoint to the requested generation level

  - Requested ramp time for the PV inverter to move from the current setpoint to the new setpoint if either it is now being constrained or it is now being released from a constraint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the PV inverter will revert to its default status, such as resetting the maximum power setpoint to its default value (optional – if not included, then default timeout period for this function will be used)

- Receive response to the command:

  - Successful (plus actual maximum power setpoint)

  - Rejected (plus reason)

### Function PC3: Adjust Power Factor

Fixed power factor will be managed through issuing a power factor angle value. In addition, a ramp rate (angle versus time) and a delay time before starting will be included so that not all PV inverters change state abruptly or at the same time.

A timeout period is included for reverting to the default state of the PV inverter, to ensure that a missed or lost command does not impact normal operations beyond that timeout period.

The utility/ESP or the Customer EMS takes the following actions:

- (Optional) Request status of PV inverter: Request a pre-defined set of the status information, including the status values, the quality flag, and the timestamp of the status (see Function PC6 for details of status points).

- Issue command to adjust power factor setpoint:

  - Command to adjust the power factor angle

  - Requested ramp time for the PV inverter to move from the current setpoint to the new setpoint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the PV inverter will revert to its default status, such as resetting the power factor setpoint to its default value (optional – if not included, then default timeout period for this function will be used)

- Receive response to the command:

  - Successful (plus actual output power factor value)

  - Rejected (plus reason)

## PV/Storage Functions

Both autonomous and directly managed PV/Storage systems (see Section 1.3) require object modeling standards for their interactions with external systems, but only the directly managed PV/Storage system will need object modeling standards for direct interactions.

It is understood that PV/Storage systems will always be in ultimate control of what they do and that these functions are “requests” to perform certain actions if feasible within pre-specified constraints.  For example, a storage system cannot charge when the storage element is full nor can it discharge if at the storage reserve limit.

### Function PC4a: Request Real Power (Charge or Discharge Storage)

This function requests the storage system to charge or discharge and at what rate (% of max charging rate).  A controller might use this command frequently, in conjunction with reads of the battery charge level, to achieve a desired daily charge / dump characteristic.

To account for diversity in the size of storage systems, the function requests a percentage quantity based on the capacity of the system.  For real power out requests (storage discharging), the percent is relative to the maximum discharge rate (inverter capacity).  For real power in requests (storage charging), the percent is relative to the maximum charging rate (battery charger capacity).  It is acknowledged that the discharging capacity of the inverter and the charging capacity of the charger may differ.

A timeout period is included for reverting to the default state of the PV inverter, to ensure that a missed or lost command does not impact normal operations beyond that timeout period.

The PV/Storage system may also determine if only PV inverter output is used for charging or whether grid power can be used.

The utility/ESP or the Customer EMS takes the following actions:

- (Optional) Request status of PV/Storage system: Request a pre-defined set of the status information, including the status values, the quality flag, and the timestamp of the status (see Function PC6 for details of status points).

- Issue command to request real power (charge/discharge) setpoint for the storage system:

  - Command to adjust the real power charge/discharge setpoint for the storage system

  - Requested ramp time for the PV/storage system to move from the current setpoint to the new setpoint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the PV/Storage system will revert to its default status (optional – if not included, then default timeout period for this function will be used)

  - Storage charge from grid setting (yes/no)

- Receive response to the command:

  - Successful (plus actual real power setpoint)

  - Rejected (plus reason)

### Function PC4b: Provide Pricing Signal

This function provides a pricing signal (actual price or some relative pricing indication) from which the PV/Storage system may decide whether to charge the storage or discharge the storage, and what rate to charge or discharge.

The utility/ESP or the Customer EMS takes the following actions:

- Issue pricing signal (the actual form or content of the pricing signal will be established by the utility/ESP and is outside the scope of this specification):

  - Pricing signal

  - Requested ramp time for the PV/storage system to move from its current output to any new output (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the PV/Storage system will revert to its default status (optional – if not included, then default timeout period for this function will be used)

- Receive response to the command:

  - Successful (plus actual real power setpoint)

  - Rejected (plus reason)

### Function PC4c: Modify PV/Storage Settings

This function permits the utility, energy service provider, customer EMS, and/or other authorized entities to dynamically modify or update various parameters for PV/Storage systems. This list of parameters may be expanded, but will include:

Intermittency Ramp Rate Limit.  This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.  The configuration will be in units of “percent of name-plate rating per minute”.  A single setting will be applied to both increasing and decreasing power output.  This ramp rate limit does not apply to output power changes in-response to commands that are received.  Such commands contain their own ramp limits.  PV/Storage systems must manage the details of their battery charging such that the rate of change in power delivery to and from the grid remains below this limit – even when the PV generation is intermittent.

Storage Reserve (Minimum energy charge level allowed, % of maximum charge level).  This level may be set by the vendor, asset owner, or system operator for a variety of purposes.  In some cases, depth of discharge may be limited in order to extend battery service life.  In other cases, a minimum reserve may be desired to provide some carryover during outage.  It is intended that reserve settings be maintained even while managing intermittency ramp rate limits as described above.  For example, a system with a 20% minimum reserve setting may charge up to 40% before beginning to generate to the grid so that a sudden loss of the PV source can be covered by a controlled ramp-down of generation, and yet without dropping below 20% charge.

Maximum Generation/Discharge Level at the PV/Storage system. This function is equivalent to PC2, but includes storage.

Other?

## Reporting Functions

### Function PC5: Event/History Logging

Basic requirements for event logging:

- All logs contain date and timestamps

- All logs contain unique description or event code to identify the event, including cause of event and other distinguishing characteristics

(Event codes may be standardized in the future) – maybe go to the CIM MHEC codes, but there will also be vendor-specific codes (Brian and Glenn will ask the larger group)

Deviations from scheduled requests/commands

Power out/on

Requests/commands received

Equipment failure

Harmonics (current as well as voltage distortions beyond 1547 parameters)?

EMI

- All errors or failures must be logged

- All startup and shutdown actions must be logged

- All control actions must be logged, whether triggered by external commands from the “Customer EMS”, or internal responses to external events (e.g. loss of external frequency, exceeding the temperature limit, etc.)

- All responses to control actions must be logged, whether they were successful or rejected (with explanation of cause of rejection)

- All limit violations must be logged, including returns within limits

- Specific examples:

  - Inverter Start Up time and date

  - Inverter Controlled Shut Down time and date

  - IEEE 1547 caused shut downs: time/date, duration (voltage sag, power outage, etc)

  - Utility commands for action time and date

  - Equipment failure

  - PV/Inverter failure, failure type time and date

  - Equipment Trip Out: overload due to excessive power, temperature limits exceeded, inadequate DC bus voltage: cause, time and date

  - Inability to fulfill dispatch schedule or peak demand request: cause, time and date

The retrieval of the Event/History log consists of the following command and response:

- Retrieve Event/History log

  - Retrieval command

  - Start time/ stop time (start time = 0 means start from beginning of log; stop time = 0 means include through the final log entry)

  - Type or subset of entries?

- Receive response to the command:

  - Requested log entries

  - Failed (plus reason)

### Function PC6: Status Reporting

Many functions require the status of the PV inverter either periodically, on significant change of a value, or upon request. In these cases, at least the following data can be reported:

- PV inverter status:

  - Current connect mode – Connected/disconnected

  - Inverter stand-by status – True: stand-by active

  - DC current level available for operation  – True: sufficient current

  - Output power setpoint

  - Output reactive power setpoint

  - Power factor setpoint as angle (optional)

  - Frequency setpoint (optional)

- Power measurements:

  - Total Active Power (Total P): Value, High and Low Limits

  - Total Reactive Power (Total Q): Value, High and Low Limits

  - Average Power factor (Total PF), Value, High and Low Limits

  - Phase to ground voltages (VL1ER, …): Value, High and Low Limits

- Battery storage status (if storage is included in PV system):

  - Amp-hour capacity rating

  - Minimum resting amp-hour capacity rating allowed

  - Nominal voltage of battery

  - Maximum battery discharge current

  - Maximum battery charge voltage

  - High battery voltage alarm level

  - Low battery voltage alarm level

  - External battery voltage

  - Rate of output battery voltage change

  - Internal battery voltage

  - Battery drain current

  - Internal battery current

State of charge (energy % of maximum charge level)

Reserve (Minimum energy charge level allowed, % of maximum charge level)

Available Energy (State of charge – Reserve)

Intermittency ramp rate

Maximum generation setting

General information

Time resolution and source of time synchronization

The report of status consists of the following command and response:

- Provide status

  - Status command

  - Type or subset of status?

- Receive response to the command:

  - Requested status information

  - Failed (plus reason)

## Periodic Commands

### Function PC7: Time Synchronization

The PV inverter will use of Network Time Protocol (NTP) (RFC-1305) or Simple Network Time Protocol (SNTP) (RFC 1305) between the “customer EMS” and the PV inverter to set time.

## VAR Modes for Decentralized Var Support from PV/Storage Inverters

### VAR Management Modes and Volt/Var Arrays (SubModes)

Since utilities (and/or other energy service providers) will be requesting var support from many different PV inverters with different capabilities, different ranges, and different local conditions, it would be very demanding of the communications systems, unnecessary, and ultimately impossible for the utilities to issue explicit settings to each PV inverter every time a change is desired.

PV Modes and SubModes: Therefore, PV Modes have been established (see Modes PV1 – PV4) for typical types of var support requests. For each PV mode, one to a few volt/var arrays of settings (termed SubModes) can be associated. Each volt/var array consists of volt/var pairs: a set of voltage levels and their corresponding var levels that will be treated as a piecewise linear function. These arrays can be of variable length, depending upon the number of volt/var pairs. Utilities can issue these volt/var array SubModes initially and update them when necessary.

Invoking PV Modes: There are three ways a utility can invoke a PV Mode and its SubMode:

Direct requests to specific PV inverters

Broadcasts or multicasts to all PV inverters in a selected area (region, feeder, substation) to use a particular volt/var array.

Scheduling PV Modes and SubModes using different criteria.

Requested PV Modes will remain in effect until superseded by another requested PV Mode.

Loosely coupled actions: PV Mode requests to PV inverters are examples of decentralized coordination of generation or loosely-coupled generation control. These are characterized by “request signals” rather than “explicit commands” sent to generation sources. The difference is that “request signals” may or may not be followed due either to limitations of the equipment (or sunlight) or to customer decisions; while “explicit commands” must be followed.

These SubMode volt/var arrays and the PV Modes are not explicit for a particular PV inverter or even type or size of PV inverter, but are focused on requesting all PV inverters to provide the needed var support as best as their capabilities allow them. For instance, PV inverters may not be able to respond for any number of reasons: the sun is not shining, the customer has overridden the mode setting, local situations are impacting what response the PV inverter can provide, etc. Therefore the utility is expecting to get an aggregated response from many or most PV inverters, but not all. Any financial ramifications will be determined by the metering results.

Since these mode requests maybe broadcast to specific groups of PV inverters and since the responses from the PV inverters will generally not be explicit, the utility may not know what the actual responses will end up being, and could require subsequent interactions not only with these PV inverters but possibly with distribution grid capacitor controllers, load tap changers, voltage regulators, storage devices, and other types of DER.

Randomized response times: For broadcast PV Mode requests, since the mode requests will (most likely) be broadcast to large numbers of PV inverters at the same time, it may be necessary to stagger the responses by the PV inverters and/or allow local conditions to dictate whether they respond at all. This is the same issue as load control systems have dealt with for many years, so many of the same solutions may be applicable.

Ramp rate: In addition to the volt/var settings, a ramp rate (the time in seconds required for the inverter to reach 63% of the demanded var output (RC time constant)) or a randomization interval (time window, in seconds, during which the inverter would randomly initiate the identified actions) would be provided to smooth and stabilize the responses of large numbers of PV inverters.

IEEE 1547: This specification addresses PV Modes that operate only within the “IEEE 1547 Green Zone”. Therefore for informational purposes, the following definitions are used:

Vmin is the IEEE 1547 minimum voltage level of 88% of nominal voltage where the PV inverter must disconnect.

Vmax is the IEEE 1547 maximum voltage level of 110% of nominal voltage where the PV inverter must disconnect.

Qmax is the inverter’s current var capability and may be positive (capacitive) or negative (inductive). It would be the kVA capability left after supporting the kW demand.

Key PV Modes are described below, with the understanding that additional modes may be defined at a later date.  In any of these modes, the PV inverter would still be limited to what it can safely or physically provide, and will log its actions.

Timeout period: A timeout period is included for reverting to the default state of the PV inverter, to ensure that a missed or lost command does not impact normal operations beyond that timeout period.

### VAR Mode PV1: Normal Energy Conservation Mode

The Normal Energy Conservation mode reflects the utility’s calculation of the most efficient and reliable var levels for PV inverters at specific distribution points of common coupling (PCC). This mode could also help compensate for local high voltage due to PV kW back flow on the circuit.

In this mode, PV inverters will be provided with a double array of setpoints: a set of voltage levels and their corresponding var levels. The voltage levels will range between V1 and V2 in increasing voltage values. Values between these setpoints will be interpolated to create at a piecewise linear volt/var function. The corresponding var levels would define the percent of Qmax (ranging between -100% and +100%) being requested for the voltage level.

The figure below is one example of volt/var settings for this mode. It is assumed that the var value between Vmin and V1 is the same as for V1 (Qmax in this example). The equivalent is true for the var value between V4 and Vmax (-Qmax in this example).

- Issue request to go into PV1 Mode:

  - Request to go into PV1 Mode

  - Array of volt/var of setpoints (optional – if not included, then use previously established default array)

  - Requested ramp time for the PV inverter to move from the current setpoint to the new setpoint if either it is now being constrained or it is now being released from a constraint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the PV inverter will revert to its default status, such as resetting the maximum power setpoint to its default value (optional – if not included, then default timeout period for this function will be used)

### VAR Mode PV2: Maximum Var Support Mode

In this mode, PV inverters provide maximum vars currently available (Qmax available = 100%) without reducing kW output or exceeding Vmax. This mode would typically be invoked by the utility to support transmission var emergencies.

This function would essentially be represented as a straight horizontal line at Qmax = 100%, until the IEEE 1547 low voltage limit or ANSI C84.1 high voltage limit is reached or the inverter protective limits are hit (although the actual var value of Qmax itself could vary at different voltage levels).

The figure below provides one example of how a PV2 mode may be configured.   In this example, the inverter generates maximum capacitive vars for reduced voltages down to the cutoff limit Vmin.  As voltage increases above configuration point V1, var generation is ramped down, reaching zero at V2, so as not to drive the local system voltage too high.

The ramp rates and/or the randomized time-constant settings are also required.

- Issue request to go into PV2 Mode:

  - Request to go into PV2 Mode

  - Array of volt/var of setpoints (optional – if not included, then use previously established default array)

  - Requested ramp time for the PV inverter to move from the current setpoint to the new setpoint if either it is now being constrained or it is now being released from a constraint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the PV inverter will revert to its default status, such as resetting the maximum power setpoint to its default value (optional – if not included, then default timeout period for this function will be used)

### VAR Mode PV3: Static Var Mode

In this mode, inverters will be set with fixed var settings.

This function can be typically represented as a straight horizontal line at a Q percentage value between +/-100% until the IEEE P1547 Vmin/Vmax levels or the inverter protective limits are reached.  It is distinguished from mode PV4 only in that the Var level is assumed to be non-zero.

This mode is likely to be of interest in cases where a separate PV system controller is managing the PV site.  In such a case, the controller would be the point of intelligence, monitoring system voltage and communicating with the utility, then managing the local inverters moment by moment to achieve the desired results.

The figure below illustrates a case where mode PV3 is configured using two voltage points with the same var setting for each.  This results in a flat var generation across the entire inverter operating range because of the previously defined flat behavior above the highest voltage configuration point and below the lowest.

The ramp rates and/or the randomized time-constant settings are also required.

- Issue request to go into PV3 Mode:

  - Request to go into PV3 Mode

  - Array of volt/var of setpoints (optional – if not included, then use previously established default array)

  - Requested ramp time for the PV inverter to move from the current setpoint to the new setpoint if either it is now being constrained or it is now being released from a constraint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the PV inverter will revert to its default status, such as resetting the maximum power setpoint to its default value (optional – if not included, then default timeout period for this function will be used)

### VAR Mode PV4: Passive Mode

This mode is the same as mode PV3 above, except that the var levels are zero.  Although managing the configuration of this mode using a volt/var array is overkill, it is used here for consistency with other modes.  Any attempt to configure mode PV3 with non-zero var levels will result in an error response.

In this mode, inverters will follow the system voltage levels within their capability range, presumably at their most efficient settings. This would be the same as current UL 1741/IEEE 1547 compliant product.

This mode will serve as the default mode for PV inverters upon power up, when schedules expire, or if no communications have been received within a defined period.  (e.g. if no additional signals have been received over x hours or if the schedule has run out without further updates).

Utilities could switch some or all inverters to this mode if other modes presented unexpected difficulties.

- Issue request to go into PV4 Mode:

  - Request to go into PV4 Mode

  - Array of volt/var of setpoints (optional – if not included, then use previously established default array)

  - Requested ramp time for the PV inverter to move from the current setpoint to the new setpoint if either it is now being constrained or it is now being released from a constraint (optional – if not included, then use previously established default ramp rate)

  - Time window within which to randomly execute the command. If the time window is zero, the command will be executed immediately, (optional – if not included, then default time window for this function will be used)

  - Timeout period, after which the PV inverter will revert to its default status, such as resetting the maximum power setpoint to its default value (optional – if not included, then default timeout period for this function will be used)

# Scheduled Actions

## Scheduling Using Time and Temperature for Var Modes

Larger PV systems and large aggregations of small PV systems have significant influence on the distribution system and have local volt/var characteristics that may vary throughout the day.  As a result, a single volt/var configuration may not be suitable at all times. Sending many control commands may impact the communications system or may not be received in a timely manner, leading to inadequate PV system responses. However, if schedules can be established that the PV systems can follow autonomously, then these communication impacts can be minimized.

Therefore, in addition to direct control or broadcast/multicast requests, utilities and/or ESPs could send out schedules to individual and/or large groups of PV inverters, based on time, temperature, pricing signal, or possibly other criteria. This method allows more autonomous control with less tightly-coupled coordination, while requiring fewer interactions.

For var support actions, PV inverters could act in a similar manner to feeder capacitor banks, changing var settings based on a time schedule and/or temperature. This capability would most likely be used with larger installations of PV inverters, for instance at a PV inverter farm, where the utility could manage the PV inverters as part of primary feeder volt/var schemes.  The reason for this mode is that voltage sensed by these large inverters will differ from that sensed by nearby customers due to voltage drop on transformers and secondaries.  This is the same problem with voltage switched capacitor banks.

These schedules can be  used as follows:

- Initially, and as needed over time, the utility or ESP issues volt/var arrays (SubModes) for each of the PV Modes that could be used in schedule (up to a limit of arrays determined during implementation).

- These schedules consist of base/mode arrays: with pairs of the base (times or temperatures) linked to these PV Modes and SubModes.

Two types of schedules are covered in this specification (although others could be developed later): time-based and temperature-based.  The two schedules are:

- Time-based Scheduling: The PV inverter may be sent a variable-length array of times (t) in seconds (e.g. t0= 0; t1=7200, t2=36,000, etc.) with a Mode and SubMode associated with each time. This time-based schedule uses relative time, so that all times (t) are added to some start time (e.g. if start time is 6:00 am, then t0 = 6 am, t1 = 8 am, t2 = 4 pm). The PV inverter would follow this schedule indefinitely until some new command is received or power is cycled.

- Temperature-based Scheduling: If the PV installation has access to ambient temperature readings either locally or provided by the utility, the schedule of Modes/SubModes could be temperature-based. The schedule would then consist of pairs of temperature and associated PV Mode and SubMode.

## Scheduling for Charging / Discharging in PV/Storage Systems

This is a scheduled version of the “Request Real Power” function.  By sending a schedule to a device for charging and discharging, as opposed to immediate settings, the burden on the communication system may be reduced.  The settings for this function are still a percentage (based on system capacity), just as with the “Request Real Power” message.

## Scheduling Using Pricing Signals (or Value) of Energy

This is the scheduled version of the “Provide Pricing Signal” function. Pricing Signal Schedules use an absolute price or some relative value of energy to allow autonomous systems to decide what actions to take. The pricing signal may reflect the actual price of energy in a TOU, CPP or dynamic pricing program, or it may be an abstract indicator of how the value of energy varies throughout the day or week.

The pricing signals in the schedule may be common across a wide geographical area, or may vary by location (Locational Marginal Pricing (LMP)), or may take into account specific substation or feeder requirements and/or constraints.  Autonomous storage systems will apply this information to make decisions, likely in conjunction with other configuration and preference data, using vendor-specific methods to manage the actual charging and discharging of the storage element.